## Components
File Name | Page Number | Asset Name | Component Name | Maker | Model | Qty | Serial Number | Specification | Base Component | Function | Component Type | Alias Component Name | System name | Manufacture date | Findings | Confidence
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 13 | CENTRIFUGAL PUMPS | Valves | TAIKO KIKAI INDUSTRIES CO.,LTD. | [5 empty] | Control fluid flow; prevent air invasion (suction side); discharge air (air vent valve); adjust flow (discharge side); prevent reverse flow (non-return valve) | VALVE | cocks
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 3 | CENTRIFUGAL PUMPS | Flexible Coupling | TAIKO KIKAI INDUSTRIES CO.,LTD. |  |  |  | Alignment tolerances (motor output <37kW): periphery <0.05mm, end face <0.10mm; Alignment tolerances (motor output >37kW): periphery <0.07mm, end face <0.16mm |  | Connects pump and motor shafts, allowing for minor misalignment | COUPLING
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 13 | CENTRIFUGAL PUMPS | Rigid Coupling | TAIKO KIKAI INDUSTRIES CO.,LTD. |  |  |  | Run-out of shaft center between Impeller and motor shaft (Below 37kW): Below 0.03mm; Run-out of shaft center between Impeller and motor shaft (Above 37kW): Below 0.05mm |  | Connects the pump shaft to the motor shaft, providing a fixed connection. | COUPLING
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 3 | CENTRIFUGAL PUMPS | Impeller shaft | TAIKO KIKAI INDUSTRIES CO.,LTD. |  |  |  | Run-out of center from casing center (Below 37kW): Below 0.03mm; Run-out of center from casing center (Above 37kW): Below 0.05mm |  | Transmits rotational power to the impeller | SHAFT
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 3 | CENTRIFUGAL PUMPS | Impeller | TAIKO KIKAI INDUSTRIES CO.,LTD. |  |  |  | Run-out of center from casing center (Below 37kW): Below 0.03mm; Run-out of center from casing center (Above 37kW): Below 0.05mm; Clearances Between Impeller Mouth and Casing Ring (Unit[mm]): Dia. of Sliding Face 30-50, Clearance 0.27-0.38 (Standard), 0.40-0.51 (SCS combined with SUS), 0.35-0.46 (Vertical ESC-O, ESO/EMO), 0.50-0.61 (Relevant models of © where material is SCS combined with SUS), Limit Clearance in Service 1.5; Dia. of Sliding Face 50-80, Clearance 0.30-0.42 (Standard), 0.45-0.57 (SCS combined with SUS), 0.40-0.57 (Vertical ESC-O, ESO/EMO), 0.55-0.67 (Relevant models of © where material is SCS combined with SUS), Limit Clearance in Service 1.6; Dia. of Sliding Face 80-120, Clearance 0.35-0.50 (Standard), 0.50-0.65 (SCS combined with SUS), 0.45-0.60 (Vertical ESC-O, ESO/EMO), 0.60-0.75 (Relevant models of © where material is SCS combined with SUS), Limit Clearance in Service 1.9; Dia. of Sliding Face 120-150, Clearance 0.40-0.57 (Standard), 0.55-0.72 (SCS combined with SUS), 0.55-0.72 (Vertical ESC-O, ESO/EMO), 0.70-0.87 (Relevant models of © where material is SCS combined with SUS), Limit Clearance in Service 2.0; Dia. of Sliding Face 150-250, Clearance 0.50-0.69 (Standard), 0.65-0.84 (SCS combined with SUS), 0.65-0.84 (Vertical ESC-O, ESO/EMO), 0.80-0.99 (Relevant models of © where material is SCS combined with SUS), Limit Clearance in Service 2.4; Dia. of Sliding Face 250-315, Clearance 0.60-0.82 (Standard), 0.80-1.02 (SCS combined with SUS), 0.80-1.02 (Vertical ESC-O, ESO/EMO), 0.95-1.17 (Relevant models of © where material is SCS combined with SUS), Limit Clearance in Service 2.8; Dia. of Sliding Face 315-400, Clearance 0.70-0.93 (Standard), 0.90-1.13 (SCS combined with SUS), 0.90-1.13 (Vertical ESC-O, ESO/EMO), 1.05-1.28 (Relevant models of © where material is SCS combined with SUS), Limit Clearance in Service 3.0; Dia. of Sliding Face 400-500, Clearance 0.80-1.06 (Standard), 1.10-1.36 (SCS combined with SUS), 1.10-1.36 (Vertical ESC-O, ESO/EMO), 1.25-1.51 (Relevant models of © where material is SCS combined with SUS), Limit Clearance in Service 3.4 |  | Increases the pressure and flow of the fluid | IMPELLER
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 3 | CENTRIFUGAL PUMPS | Casing | TAIKO KIKAI INDUSTRIES CO.,LTD. |  |  |  | Internal surface shall be coated with tar epoxy resin coating if made of cast iron and processing sea water. |  | Contains the fluid and directs its flow | CASING
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 13 | CENTRIFUGAL PUMPS | Casing ring | TAIKO KIKAI INDUSTRIES CO.,LTD. |  |  |  | Clearances Between Impeller Mouth and Casing Ring (Unit[mm]): Dia. of Sliding Face 30-50, Clearance 0.27-0.38 (Standard), 0.40-0.51 (SCS combined with SUS), 0.35-0.46 (Vertical ESC-O, ESO/EMO), 0.50-0.61 (Relevant models of © where material is SCS combined with SUS), Limit Clearance in Service 1.5; Dia. of Sliding Face 50-80, Clearance 0.30-0.42 (Standard), 0.45-0.57 (SCS combined with SUS), 0.40-0.57 (Vertical ESC-O, ESO/EMO), 0.55-0.67 (Relevant models of © where material is SCS combined with SUS), Limit Clearance in Service 1.6; Dia. of Sliding Face 80-120, Clearance 0.35-0.50 (Standard), 0.50-0.65 (SCS combined with SUS), 0.45-0.60 (Vertical ESC-O, ESO/EMO), 0.60-0.75 (Relevant models of © where material is SCS combined with SUS), Limit Clearance in Service 1.9; Dia. of Sliding Face 120-150, Clearance 0.40-0.57 (Standard), 0.55-0.72 (SCS combined with SUS), 0.55-0.72 (Vertical ESC-O, ESO/EMO), 0.70-0.87 (Relevant models of © where material is SCS combined with SUS), Limit Clearance in Service 2.0; Dia. of Sliding Face 150-250, Clearance 0.50-0.69 (Standard), 0.65-0.84 (SCS combined with SUS), 0.65-0.84 (Vertical ESC-O, ESO/EMO), 0.80-0.99 (Relevant models of © where material is SCS combined with SUS), Limit Clearance in Service 2.4; Dia. of Sliding Face 250-315, Clearance 0.60-0.82 (Standard), 0.80-1.02 (SCS combined with SUS), 0.80-1.02 (Vertical ESC-O, ESO/EMO), 0.95-1.17 (Relevant models of © where material is SCS combined with SUS), Limit Clearance in Service 2.8; Dia. of Sliding Face 315-400, Clearance 0.70-0.93 (Standard), 0.90-1.13 (SCS combined with SUS), 0.90-1.13 (Vertical ESC-O, ESO/EMO), 1.05-1.28 (Relevant models of © where material is SCS combined with SUS), Limit Clearance in Service 3.0; Dia. of Sliding Face 400-500, Clearance 0.80-1.06 (Standard), 1.10-1.36 (SCS combined with SUS), 1.10-1.36 (Vertical ESC-O, ESO/EMO), 1.25-1.51 (Relevant models of © where material is SCS combined with SUS), Limit Clearance in Service 3.4 | Casing | Provides a wear surface and helps maintain efficiency by reducing internal leakage within the pump casing. | WEAR RING
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 13 | CENTRIFUGAL PUMPS | Vacuum pump | TAIKO KIKAI INDUSTRIES CO.,LTD. |  |  |  |  | Self-priming unit | Used for priming the centrifugal pump by removing air from the suction line. | PUMP
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 3 | CENTRIFUGAL PUMPS | Pressure gauge | TAIKO KIKAI INDUSTRIES CO.,LTD. | [5 empty] | Measures fluid pressure | GAUGE
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 3 | CENTRIFUGAL PUMPS | Bearing | TAIKO KIKAI INDUSTRIES CO.,LTD. |  |  |  | Permissible bearing temperature: ambient +40°C or liquid +20°C, max 75°C |  | Supports the rotating shaft and reduces friction | BEARING
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 3 | CENTRIFUGAL PUMPS | Roller bearing | TAIKO KIKAI INDUSTRIES CO.,LTD. |  |  |  | Recommended lubricant: Turbine ISO VG46, Roller bearing grease Type 1 No.2 | Bearing | Supports the rotating shaft and reduces friction | BEARING
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 3 | CENTRIFUGAL PUMPS | Submerged line bearing | TAIKO KIKAI INDUSTRIES CO.,LTD. |  |  |  | Diameter 30-50, clearance by metal (in diameter) 0.05-0.10; Diameter 50-80, clearance by metal (in diameter) 0.10-0.15; Diameter 80-120, clearance by metal (in diameter) 0.15-0.25 | Bearing | Supports the shaft in submerged applications | BEARING
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 13 | CENTRIFUGAL PUMPS | Gland Packing | TAIKO KIKAI INDUSTRIES CO.,LTD. |  |  |  | Reference Leak Amount (cc/min) In operation: Shaft Dia. 24-40 (12-20), 41-60 (15-25), 61-70 (18-30); In standstill: Shaft Dia. 24-40 (24-34), 41-60 (30-40), 61-70 (35-45). Cut end of each packing should be apart by 120 degrees. | Stuffing Box | Seals the shaft where it exits the pump casing to prevent leakage | SEAL | packing
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 13 | CENTRIFUGAL PUMPS | Mechanical seal | TAIKO KIKAI INDUSTRIES CO.,LTD. |  |  |  | Allowable Leak (Water, N Slurry): 3 cc/Hr (1 drop/min.); Allowable Leak (Water, Y Slurry): 5 cc/Hr (1 drop/30-40 sec.); Allowable Leak (Hot water, N Slurry): 3 cc/Hr (1 drop/min.); Allowable Leak (Hot water, Y Slurry): 5 cc/Hr (1 drop/30-40 sec.) | Stuffing Box | Seals the rotating shaft to prevent fluid leakage | SEAL
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 13 | CENTRIFUGAL PUMPS | Shaft | TAIKO KIKAI INDUSTRIES CO.,LTD. |  |  |  | Shaft wear limit: 2mm diameter defacement. Alignment tolerances (motor output <37kW): shaft center run-out <0.03mm. Alignment tolerances (motor output >37kW): shaft center run-out <0.05mm. |  | Transmits rotational power from the motor to the pump impeller. | SHAFT | pump shaft
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 3 | CENTRIFUGAL PUMPS | O-ring | TAIKO KIKAI INDUSTRIES CO.,LTD. |  |  |  |  | Gear coupling | Provides a static seal to prevent leakage | SEAL
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 3 | CENTRIFUGAL PUMPS | Shaft coupling bolts and rubber ring | TAIKO KIKAI INDUSTRIES CO.,LTD. |  |  |  |  | Shaft coupling | Connects coupling halves and provides flexibility/dampening | COUPLING COMPONENT
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 3 | CENTRIFUGAL PUMPS | Gear coupling | TAIKO KIKAI INDUSTRIES CO.,LTD. |  |  |  | Type of grease: JIS K2220 central lubrication grease Type 4 No.1, or equivalent. Grease Amount (g): KSE-103 (29), KSE-115 (57), KSE-125 (70), KSE-137 (90), KSE-160 (S) (165), KSE-175 (175), KSE-190 (206), KSE-224 (313) |  | Transmits torque between two shafts, allowing for angular and parallel misalignment | COUPLING
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 3 | CENTRIFUGAL PUMPS | Sleeve A | TAIKO KIKAI INDUSTRIES CO.,LTD. |  |  |  |  | Gear coupling | Part of the gear coupling assembly | COUPLING COMPONENT
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 3 | CENTRIFUGAL PUMPS | Solid flange | TAIKO KIKAI INDUSTRIES CO.,LTD. |  |  |  |  | Gear coupling | Connects the coupling to the shaft | COUPLING COMPONENT
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 3 | CENTRIFUGAL PUMPS | Hub | TAIKO KIKAI INDUSTRIES CO.,LTD. |  |  |  |  | Gear coupling | Connects the coupling to the shaft | COUPLING COMPONENT
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 3 | CENTRIFUGAL PUMPS | Reamer bolt | TAIKO KIKAI INDUSTRIES CO.,LTD. |  |  |  |  | Gear coupling | Secures coupling components | FASTENER
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 3 | CENTRIFUGAL PUMPS | Class 1 nut | TAIKO KIKAI INDUSTRIES CO.,LTD. |  |  |  |  | Gear coupling | Secures coupling components | FASTENER
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 13 | CENTRIFUGAL PUMPS | Side cover | TAIKO KIKAI INDUSTRIES CO.,LTD. |  |  |  |  | Gear coupling | Covers internal components and provides a seal, holds O-ring. | CASING PART
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 3 | CENTRIFUGAL PUMPS | Hexagon head cap screw | TAIKO KIKAI INDUSTRIES CO.,LTD. |  |  |  |  | Gear coupling | Secures coupling components | FASTENER
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 3 | CENTRIFUGAL PUMPS | Oil plug | TAIKO KIKAI INDUSTRIES CO.,LTD. |  |  |  |  | Gear coupling | Allows for filling or draining oil from the coupling | PLUG
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 3 | CENTRIFUGAL PUMPS | Grease nipple | TAIKO KIKAI INDUSTRIES CO.,LTD. |  |  |  |  | Gear coupling | Provides a point for lubricating the coupling with grease | FITTING
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 13 | CENTRIFUGAL PUMPS | Inner Cylinder | TAIKO KIKAI INDUSTRIES CO.,LTD. |  |  |  | Mentioned in context of gear coupling greasing for wear resistance and noise prevention. |  | Part of the rotating assembly, likely for fluid guidance or sealing, forms part of the gear coupling. | CYLINDER
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 13 | CENTRIFUGAL PUMPS | Outer Cylinder | TAIKO KIKAI INDUSTRIES CO.,LTD. |  |  |  | Mentioned in context of gear coupling greasing for wear resistance and noise prevention. |  | Part of the rotating assembly, likely for fluid guidance or sealing, forms part of the gear coupling. | CYLINDER
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 13 | CENTRIFUGAL PUMPS | Motor | TAIKO KIKAI INDUSTRIES CO.,LTD. |  |  |  | Alignment tolerances (motor output <37kW): coupling periphery <0.05mm, coupling end face <0.10mm, shaft center run-out <0.03mm, impeller center run-out <0.03mm. Alignment tolerances (motor output >37kW): coupling periphery <0.07mm, coupling end face <0.16mm, shaft center run-out <0.05mm, impeller center run-out <0.05mm. |  | Provides rotational power to drive the pump. | MOTOR
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 13 | CENTRIFUGAL PUMPS | Gear Coupling | TAIKO KIKAI INDUSTRIES CO.,LTD. | KSE-l03 |  |  | Recommended run-outs in Centering: Parallel Deviation (0) 0.04 mm, Angle Deviation (e·) 0.05·, (C2-Cl) 0.04 mm, Axial Clearance (C) 8 mm. Critical for performance, grease forms oil film on gear contact face, improves wear resistance, prevents noise, temperature rise, and self-excited vibration. |  | Connects the pump shaft to the motor shaft, allowing for slight misalignment and transmitting torque. | COUPLING
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 13 | CENTRIFUGAL PUMPS | Gear Coupling | TAIKO KIKAI INDUSTRIES CO.,LTD. | KSE-115 |  |  | Recommended run-outs in Centering: Parallel Deviation (0) 0.04 mm, Angle Deviation (e·) 0.05·, (C2-Cl) 0.05 mm, Axial Clearance (C) 8 mm. Critical for performance, grease forms oil film on gear contact face, improves wear resistance, prevents noise, temperature rise, and self-excited vibration. |  | Connects the pump shaft to the motor shaft, allowing for slight misalignment and transmitting torque. | COUPLING
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 13 | CENTRIFUGAL PUMPS | Gear Coupling | TAIKO KIKAI INDUSTRIES CO.,LTD. | KSE-125 |  |  | Recommended run-outs in Centering: Parallel Deviation (0) 0.05 mm, Angle Deviation (e·) 0.05·, (C2-Cl) 0.06 mm, Axial Clearance (C) 8 mm. Critical for performance, grease forms oil film on gear contact face, improves wear resistance, prevents noise, temperature rise, and self-excited vibration. |  | Connects the pump shaft to the motor shaft, allowing for slight misalignment and transmitting torque. | COUPLING
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 13 | CENTRIFUGAL PUMPS | Gear Coupling | TAIKO KIKAI INDUSTRIES CO.,LTD. | KSE-137 |  |  | Recommended run-outs in Centering: Parallel Deviation (0) 0.05 mm, Angle Deviation (e') 0.05', (C2-Cl) 0.06 mm, Axial Clearance (C) 8 mm. Critical for performance, grease forms oil film on gear contact face, improves wear resistance, prevents noise, temperature rise, and self-excited vibration. |  | Connects the pump shaft to the motor shaft, allowing for slight misalignment and transmitting torque. | COUPLING
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 13 | CENTRIFUGAL PUMPS | Gear Coupling | TAIKO KIKAI INDUSTRIES CO.,LTD. | KSE-160(S) |  |  | Recommended run-outs in Centering: Parallel Deviation (0) 0.06 mm, Angle Deviation (e·) 0.05·, (C2-Cl) 0.08 mm, Axial Clearance (C) 10 mm. Critical for performance, grease forms oil film on gear contact face, improves wear resistance, prevents noise, temperature rise, and self-excited vibration. |  | Connects the pump shaft to the motor shaft, allowing for slight misalignment and transmitting torque. | COUPLING
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 13 | CENTRIFUGAL PUMPS | Gear Coupling | TAIKO KIKAI INDUSTRIES CO.,LTD. | KSE-175 |  |  | Recommended run-outs in Centering: Parallel Deviation (0) 0.06 mm, Angle Deviation (e·) 0.05·, (C2-Cl) 0.09 mm, Axial Clearance (C) 10 mm. Critical for performance, grease forms oil film on gear contact face, improves wear resistance, prevents noise, temperature rise, and self-excited vibration. |  | Connects the pump shaft to the motor shaft, allowing for slight misalignment and transmitting torque. | COUPLING
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 13 | CENTRIFUGAL PUMPS | Gear Coupling | TAIKO KIKAI INDUSTRIES CO.,LTD. | KSE-190 |  |  | Recommended run-outs in Centering: Parallel Deviation (0) 0.06 mm, Angle Deviation (e·) 0.05·, (C2-Cl) 0.10 mm, Axial Clearance (C) 10 mm. Critical for performance, grease forms oil film on gear contact face, improves wear resistance, prevents noise, temperature rise, and self-excited vibration. |  | Connects the pump shaft to the motor shaft, allowing for slight misalignment and transmitting torque. | COUPLING
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 13 | CENTRIFUGAL PUMPS | Gear Coupling | TAIKO KIKAI INDUSTRIES CO.,LTD. | KSE-224 |  |  | Recommended run-outs in Centering: Parallel Deviation (0) 0.07 mm, Angle Deviation (e·) 0.05·, (C2-Cl) 0.12 mm, Axial Clearance (C) 12 mm. Critical for performance, grease forms oil film on gear contact face, improves wear resistance, prevents noise, temperature rise, and self-excited vibration. |  | Connects the pump shaft to the motor shaft, allowing for slight misalignment and transmitting torque. | COUPLING
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 13 | CENTRIFUGAL PUMPS | Flange | TAIKO KIKAI INDUSTRIES CO.,LTD. | [5 empty] | Connects the outer cylinder to the solid flange, ensuring a sealed connection. | CONNECTION PART
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 13 | CENTRIFUGAL PUMPS | Impeller | TAIKO KIKAI INDUSTRIES CO.,LTD. | TMS-40A |  |  | Semi-open type. Alignment tolerances (motor output <37kW): impeller center run-out <0.03mm. Alignment tolerances (motor output >37kW): impeller center run-out <0.05mm. Clearance between back of impeller and casing cover should be 0.6 to 0.7 mm. |  | Increases the pressure and flow rate of the fluid by converting rotational energy into kinetic energy. | IMPELLER
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 13 | CENTRIFUGAL PUMPS | Impeller | TAIKO KIKAI INDUSTRIES CO.,LTD. | TMS-50B(4P) |  |  | Semi-open type. Alignment tolerances (motor output <37kW): impeller center run-out <0.03mm. Alignment tolerances (motor output >37kW): impeller center run-out <0.05mm. Clearance between back of impeller and casing cover should be 0.6 to 0.7 mm. |  | Increases the pressure and flow rate of the fluid by converting rotational energy into kinetic energy. | IMPELLER
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 13 | CENTRIFUGAL PUMPS | Impeller | TAIKO KIKAI INDUSTRIES CO.,LTD. | TMS-65B(4P) |  |  | Semi-open type. Alignment tolerances (motor output <37kW): impeller center run-out <0.03mm. Alignment tolerances (motor output >37kW): impeller center run-out <0.05mm. Clearance between back of impeller and casing cover should be 0.6 to 0.7 mm. |  | Increases the pressure and flow rate of the fluid by converting rotational energy into kinetic energy. | IMPELLER
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 13 | CENTRIFUGAL PUMPS | Impeller | TAIKO KIKAI INDUSTRIES CO.,LTD. | TMS-80B |  |  | Semi-open type. Alignment tolerances (motor output <37kW): impeller center run-out <0.03mm. Alignment tolerances (motor output >37kW): impeller center run-out <0.05mm. Clearance between back of impeller and casing cover should be 0.6 to 0.7 mm. |  | Increases the pressure and flow rate of the fluid by converting rotational energy into kinetic energy. | IMPELLER
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 13 | CENTRIFUGAL PUMPS | Casing Cover | TAIKO KIKAI INDUSTRIES CO.,LTD. |  |  |  | Clearance between the back of impeller and the casing cover should be 0.6 to 0.7 mm. |  | Forms part of the pump housing, enclosing the impeller and directing fluid flow. | CASING PART
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 13 | CENTRIFUGAL PUMPS | Suction Pipe | TAIKO KIKAI INDUSTRIES CO.,LTD. | [5 empty] | Conveys fluid from the source to the pump's suction inlet. | PIPING
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 13 | CENTRIFUGAL PUMPS | Strainer | TAIKO KIKAI INDUSTRIES CO.,LTD. | [5 empty] | Filters debris from the fluid entering the pump to prevent clogging. | FILTER
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 13 | CENTRIFUGAL PUMPS | Gauges | TAIKO KIKAI INDUSTRIES CO.,LTD. | [5 empty] | Measures and displays operational parameters such as pressure or vacuum. | GAUGE
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 13 | CENTRIFUGAL PUMPS | Stuffing Box | TAIKO KIKAI INDUSTRIES CO.,LTD. | [5 empty] | Houses the gland packing or mechanical seal to prevent leakage along the pump shaft. | SEALING ASSEMBLY
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 13 | CENTRIFUGAL PUMPS | Pump Casing | TAIKO KIKAI INDUSTRIES CO.,LTD. | [5 empty] | Houses the impeller and directs the fluid flow, converting kinetic energy into pressure. | CASING
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 13 | CENTRIFUGAL PUMPS | Pump Bearings | TAIKO KIKAI INDUSTRIES CO.,LTD. |  |  |  | Permissible bearing temperature: ambient +40°C or liquid +20°C, max 75°C. Recommended lubricants: Turbine ISO VG46, Roller bearing grease Type 1 No.2. |  | Supports the pump shaft and allows for smooth rotation, reducing friction. | BEARING | Bearings
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 13 | CENTRIFUGAL PUMPS | Ball Bearing | TAIKO KIKAI INDUSTRIES CO.,LTD. |  |  |  | Permissible bearing temperature: ambient +40°C or liquid +20°C, max 75°C. Recommended lubricants: Turbine ISO VG46, Roller bearing grease Type 1 No.2. | Pump Bearings | Supports the pump shaft and allows for smooth rotation, reducing friction. | BEARING
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 13 | CENTRIFUGAL PUMPS | Submerged Bearing | TAIKO KIKAI INDUSTRIES CO.,LTD. |  |  |  | Permissible bearing temperature: ambient +40°C or liquid +20°C, max 75°C. Recommended lubricants: Turbine ISO VG46, Roller bearing grease Type 1 No.2. | Pump Bearings | Supports the pump shaft and allows for smooth rotation, reducing friction, designed for operation while immersed in fluid. | BEARING
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 13 | CENTRIFUGAL PUMPS | Pump Foundation | TAIKO KIKAI INDUSTRIES CO.,LTD. | [5 empty] | Provides a stable and rigid base for the pump and motor assembly, reducing vibration. | SUPPORT STRUCTURE

## Spares
File Name | Page Number | Marked Pages | Missed Extraction Pages | Asset Name | Component Name | Part Name | Part Number | Drawing Number | Position Number | Dimension | Materials | Other Details | Spare Part Title | Spare Maker | Spare Model | Working Quantity | Spare Quantity | Units | Weight | Color | Source (Table/Text) | Spare Class | Findings | Confidence
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 4 |  |  | CENTRIFUGAL PUMPS | Bearing | Roller bearing | [5 empty] | For greased bearings, replace them with new items. Type of lubricant: Turbine ISO VG46, or equivalent. Grease: Roller bearing grease Type 1 No.2, or equivalent. | Periodic Inspection | TAIKO KIKAI INDUSTRIES CO.,LTD. | [7 empty] | CRITICAL
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 4 |  |  | CENTRIFUGAL PUMPS | Bearing | Submerged line bearing |  |  |  | diameter 30-50, clearance by metal (in diameter) 0.05-0.10; diameter 50-80, clearance by metal (in diameter) 0.10-0.15; diameter 80-120, clearance by metal (in diameter) 0.15-0.25 |  | Check up sliding surfaces for points of contact and injury. Measure inside diameter and if this is about double than follow list. | Periodic Inspection | TAIKO KIKAI INDUSTRIES CO.,LTD. | [7 empty] | CRITICAL
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 14 |  |  | CENTRIFUGAL PUMPS | Stuffing Box | Gland Packing | [5 empty] | Check up condition of fitting and amount of leak. Renew it if leak is too much. | 10. Troubles and Remedies | TAIKO KIKAI INDUSTRIES CO.,LTD. | TMS-40A, 50B(4P), 65B(4P). 80B | [6 empty] | CONSUMABLE
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 14 |  |  | CENTRIFUGAL PUMPS | Stuffing Box | Mechanical seal | [5 empty] | Check up condition of mating faces. Renew it. | 10. Troubles and Remedies | TAIKO KIKAI INDUSTRIES CO.,LTD. | TMS-40A, 50B(4P), 65B(4P). 80B | [6 empty] | CRITICAL
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 14 |  |  | CENTRIFUGAL PUMPS | Pump Rotating Assembly | Shaft | [5 empty] | Check up contact points and injury in portions facing packing and bearing. Measure outside diameter and renew it in the case of this is defaced about 2 mm by the diameter. Check up points of contact, damage and bend in sliding face. | 10. Troubles and Remedies | TAIKO KIKAI INDUSTRIES CO.,LTD. | TMS-40A, 50B(4P), 65B(4P). 80B | [6 empty] | CRITICAL
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 4 |  |  | CENTRIFUGAL PUMPS | Gear Coupling | O-ring |  |  | 10 |  |  | Check up surface damage and condition of deterioration. Renew it if deformed. Renew it. | Gear Coupling - Construction | TAIKO KIKAI INDUSTRIES CO.,LTD. | [7 empty] | CONSUMABLE
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 14 |  |  | CENTRIFUGAL PUMPS | Pump Rotating Assembly | Impeller |  |  |  | Sliding Face Dia. Over 30 Up to 50: Limit Clearance in Service 1.5mm; Over 50 Up to 80: Limit Clearance in Service 1.6mm; Over 80 Up to 120: Limit Clearance in Service 1.9mm; Over 120 Up to 150: Limit Clearance in Service 2.0mm; Over 150 Up to 250: Limit Clearance in Service 2.4mm; Over 250 Up to 315: Limit Clearance in Service 2.5mm; Over 315 Up to 400: Limit Clearance in Service 3.0mm; Over 400 Up to 500: Limit Clearance in Service 3.4mm |  | Check up wear and condition of corrosion of all parts. Measure sliding face in contact with casing ring and take steps according to manufacturer's stand. | Periodic Inspection / Clearances Between Impeller Mouth and Casing Ring | TAIKO KIKAI INDUSTRIES CO.,LTD. | TMS-40A, 50B(4P), 65B(4P). 80B | [6 empty] | CRITICAL
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 14 |  |  | CENTRIFUGAL PUMPS | Pump Casing | Casing ring |  |  |  | Sliding Face Dia. Over 30 Up to 50: Limit Clearance in Service 1.5mm; Over 50 Up to 80: Limit Clearance in Service 1.6mm; Over 80 Up to 120: Limit Clearance in Service 1.9mm; Over 120 Up to 150: Limit Clearance in Service 2.0mm; Over 150 Up to 250: Limit Clearance in Service 2.4mm; Over 250 Up to 315: Limit Clearance in Service 2.5mm; Over 315 Up to 400: Limit Clearance in Service 3.0mm; Over 400 Up to 500: Limit Clearance in Service 3.4mm |  | Check up contact points, wear and condition of corrosion. Measure the interior diameter and renew it by the follow Table 3. | Periodic Inspection / Clearances Between Impeller Mouth and Casing Ring | TAIKO KIKAI INDUSTRIES CO.,LTD. | TMS-40A, 50B(4P), 65B(4P). 80B | [6 empty] | CRITICAL
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 4 |  |  | CENTRIFUGAL PUMPS | Shaft Coupling | Shaft coupling bolts | [5 empty] | Check up condition of wear and renew if abnormal points are found. | Periodic Inspection | TAIKO KIKAI INDUSTRIES CO.,LTD. | [7 empty] | CRITICAL
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 4 |  |  | CENTRIFUGAL PUMPS | Shaft Coupling | Rubber ring |  |  |  |  | RUBBER | Check up condition of wear and renew if abnormal points are found. | Periodic Inspection | TAIKO KIKAI INDUSTRIES CO.,LTD. | [7 empty] | CONSUMABLE
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 4 |  |  | CENTRIFUGAL PUMPS | Gland | Lantern ring | [5 empty] | Provide a lantern ring to feed water from outside. | Troubleshooting | TAIKO KIKAI INDUSTRIES CO.,LTD.
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 4 |  |  | CENTRIFUGAL PUMPS | Gear Coupling | Sleeve A |  |  | 1 |  |  | Replace sleeve. | Gear Coupling - Construction | TAIKO KIKAI INDUSTRIES CO.,LTD. | [7 empty] | CRITICAL
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 4 |  |  | CENTRIFUGAL PUMPS | Bearing | Bearing | [5 empty] | Replace bearing. | Troubleshooting | TAIKO KIKAI INDUSTRIES CO.,LTD. | [7 empty] | CRITICAL
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 4 |  |  | CENTRIFUGAL PUMPS | Bush | Teflon sheet bush |  |  |  |  | TEFLON | Use the teflon sheet bush. | Troubleshooting | TAIKO KIKAI INDUSTRIES CO.,LTD.
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 4 |  |  | CENTRIFUGAL PUMPS | Gear Coupling | Solid flange |  |  | 2 |  |  |  | Gear Coupling - Construction | TAIKO KIKAI INDUSTRIES CO.,LTD.
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 4 |  |  | CENTRIFUGAL PUMPS | Gear Coupling | Hub |  |  | 3 |  |  |  | Gear Coupling - Construction | TAIKO KIKAI INDUSTRIES CO.,LTD.
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 4 |  |  | CENTRIFUGAL PUMPS | Gear Coupling | Reamer bolt |  |  | 4 |  |  |  | Gear Coupling - Construction | TAIKO KIKAI INDUSTRIES CO.,LTD.
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 4 |  |  | CENTRIFUGAL PUMPS | Gear Coupling | Class 1 nut |  |  | 5 |  |  |  | Gear Coupling - Construction | TAIKO KIKAI INDUSTRIES CO.,LTD.
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 4 |  |  | CENTRIFUGAL PUMPS | Gear Coupling | Side cover |  |  | 6 |  |  |  | Gear Coupling - Construction | TAIKO KIKAI INDUSTRIES CO.,LTD.
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 14 |  |  | CENTRIFUGAL PUMPS | Pump-Motor Coupling | Hexagon head cap screw |  |  | 7 |  |  | Used to fix rigid coupling securely | Combining of Pump with Motor for Semi-open Type Impeller | TAIKO KIKAI INDUSTRIES CO.,LTD. | TMS-40A, 50B(4P), 65B(4P). 80B | [6 empty] | NON-CRITICAL
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 4 |  |  | CENTRIFUGAL PUMPS | Gear Coupling | Oil plug |  |  | 11 |  |  |  | Gear Coupling - Construction | TAIKO KIKAI INDUSTRIES CO.,LTD.
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 4 |  |  | CENTRIFUGAL PUMPS | Gear Coupling | Grease nipple |  |  | 12 |  |  |  | Gear Coupling - Construction | TAIKO KIKAI INDUSTRIES CO.,LTD.
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 14 |  |  | CENTRIFUGAL PUMPS | Electric System | Wiring | [5 empty] | Broken wiring | 10. Troubles and Remedies | TAIKO KIKAI INDUSTRIES CO.,LTD. | TMS-40A, 50B(4P), 65B(4P). 80B | [6 empty] | CRITICAL
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 14 |  |  | CENTRIFUGAL PUMPS | Electric System | Relay | [5 empty] | Relay in trouble | 10. Troubles and Remedies | TAIKO KIKAI INDUSTRIES CO.,LTD. | TMS-40A, 50B(4P), 65B(4P). 80B | [6 empty] | CRITICAL
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 14 |  |  | CENTRIFUGAL PUMPS | Piping System | Valves | [5 empty] | Valves cannot be opened | 10. Troubles and Remedies | TAIKO KIKAI INDUSTRIES CO.,LTD. | TMS-40A, 50B(4P), 65B(4P). 80B | [6 empty] | CRITICAL
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 14 |  |  | CENTRIFUGAL PUMPS | Suction System | Strainer | [5 empty] | Suction pipe or strainer is clogged | 10. Troubles and Remedies | TAIKO KIKAI INDUSTRIES CO.,LTD. | TMS-40A, 50B(4P), 65B(4P). 80B | [6 empty] | CONSUMABLE
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 14 |  |  | CENTRIFUGAL PUMPS | Instrumentation | Gauges | [5 empty] | Gauges not in function | 10. Troubles and Remedies | TAIKO KIKAI INDUSTRIES CO.,LTD. | TMS-40A, 50B(4P), 65B(4P). 80B | [6 empty] | NON-CRITICAL
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 14 |  |  | CENTRIFUGAL PUMPS | Stuffing Box | Packing | [5 empty] | Packing is too tight | 10. Troubles and Remedies | TAIKO KIKAI INDUSTRIES CO.,LTD. | TMS-40A, 50B(4P), 65B(4P). 80B | [6 empty] | CONSUMABLE
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 14 |  |  | CENTRIFUGAL PUMPS | Pump Rotating Assembly | Pump shaft | [5 empty] | Pump shaft is bent | 10. Troubles and Remedies | TAIKO KIKAI INDUSTRIES CO.,LTD. | TMS-40A, 50B(4P), 65B(4P). 80B | [6 empty] | CRITICAL
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 14 |  |  | CENTRIFUGAL PUMPS | Bearing Assembly | Pump bearings | [5 empty] | Pump bearings are wrong | 10. Troubles and Remedies | TAIKO KIKAI INDUSTRIES CO.,LTD. | TMS-40A, 50B(4P), 65B(4P). 80B | [6 empty] | CRITICAL
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 14 |  |  | CENTRIFUGAL PUMPS | Bearing Assembly | Bearings | [5 empty] | Bearings are wrong | 10. Troubles and Remedies | TAIKO KIKAI INDUSTRIES CO.,LTD. | TMS-40A, 50B(4P), 65B(4P). 80B | [6 empty] | CRITICAL
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 14 |  |  | CENTRIFUGAL PUMPS | Bearing Assembly | Ball bearing | [5 empty] | Bearings are worn | 10. Troubles and Remedies | TAIKO KIKAI INDUSTRIES CO.,LTD. | TMS-40A, 50B(4P), 65B(4P). 80B | [6 empty] | CRITICAL
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 14 |  |  | CENTRIFUGAL PUMPS | Bearing Assembly | Submerged bearing | [5 empty] | Bearings are worn | 10. Troubles and Remedies | TAIKO KIKAI INDUSTRIES CO.,LTD. | TMS-40A, 50B(4P), 65B(4P). 80B | [6 empty] | CRITICAL

## Jobs
File Name | Page Number | Marked Pages | Missed Extraction Pages | Asset Name | Component Name | Job Title | Job Type | Calendar Frequency | Calendar Frequency Type | Hour Frequency | Job Description | Safety Note | Section Name | Initial Frequency | Initial Frequency Type | Max Range Frequency | Min Range Frequency | Findings | Confidence
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 2 |  |  | CENTRIFUGAL PUMPS | Roller bearing | Replace lubricant | REPLACEMENT | 6 | MONTHLY |  | Replace lubricant *Replace lubricant first time in 3 months after operation start up. *Type of lubricant: . Lubricant: Turbine ISO VG46, or equivalent . Grease: Roller bearing grease Type 1 No.2, or equivalent. For greased bearings, replace them with new items. |  | 9.1 Periodic Inspection | 3 | Monthly
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 2 |  |  | CENTRIFUGAL PUMPS | Submerged line bearing | Check up sliding surfaces for points of contact and injury. Measure inside diameter and if this is about double than follow list. diameter clearance by metal (in diameter) 30-50 O.OS-O.lO 50-SO 0.10-0.15 SO-120 0.15-0.25 | INSPECTION | 12 | MONTHLY | 8000 | Check up sliding surfaces for points of contact and injury. Measure inside diameter and if this is about double than follow list. diameter clearance by metal (in diameter) 30-50 O.OS-O.lO 50-SO 0.10-0.15 SO-120 0.15-0.25 |  | 9.1 Periodic Inspection |  |  | 8000 | 8000
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 2 |  |  | CENTRIFUGAL PUMPS | Gland Packing | Check up condition of fitting and amount of leak. Renew it if leak is too much. | INSPECTION | 3 | MONTHLY |  | Check up condition of fitting and amount of leak. Renew it if leak is too much. |  | 9.1 Periodic Inspection
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 2 |  |  | CENTRIFUGAL PUMPS | Mechanical seal | Check up condition of mating faces. | INSPECTION | 12 | MONTHLY | 8000 | Check up condition of mating faces. |  | 9.1 Periodic Inspection |  |  | 8000 | 8000
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 2 |  |  | CENTRIFUGAL PUMPS | Mechanical seal | Renew it. | REPLACEMENT | 4 | YEARLY | 20000 | Renew it. |  | 9.1 Periodic Inspection |  |  | 20000 | 20000
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 2 |  |  | CENTRIFUGAL PUMPS | Shaft | Check up contact points and injury in portions facing packing and bearing. Measure outside diameter and renew it in the case of this is defaced about 2 mm by the diameter. | INSPECTION | 12 | MONTHLY | 8000 | Check up contact points and injury in portions facing packing and bearing. Measure outside diameter and renew it in the case of this is defaced about 2 mm by the diameter. |  | 9.1 Periodic Inspection |  |  | 8000 | 8000
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 2 |  |  | CENTRIFUGAL PUMPS | Shaft | Check up points of contact. damage and bend in sliding face. | INSPECTION | 4 | YEARLY | 20000 | Check up points of contact. damage and bend in sliding face. |  | 9.1 Periodic Inspection |  |  | 20000 | 20000
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 2 |  |  | CENTRIFUGAL PUMPS | O-ring | Check up surface damage and condition of deterioration. Renew it if deformed. | INSPECTION | 12 | MONTHLY | 8000 | Check up surface damage and condition of deterioration. Renew it if deformed. |  | 9.1 Periodic Inspection |  |  | 8000 | 8000
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 2 |  |  | CENTRIFUGAL PUMPS | O-ring | Renew it. | REPLACEMENT | 4 | YEARLY | 20000 | Renew it. |  | 9.1 Periodic Inspection |  |  | 20000 | 20000
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 2 |  |  | CENTRIFUGAL PUMPS | Impeller | Check up wear and condition of corrosion of all parts. Measure sliding face in contact with casing ring and take steps according to manufacturer's stand. | INSPECTION | 12 | MONTHLY | 8000 | Check up wear and condition of corrosion of all parts. Measure sliding face in contact with casing ring and take steps according to manufacturer's stand. |  | 9.1 Periodic Inspection |  |  | 8000 | 8000
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 2 |  |  | CENTRIFUGAL PUMPS | Casing ring | Check up contact points, wear and condition of corrosion. Measure the interior diameter and renew it by the follow Table 3. | INSPECTION | 12 | MONTHLY | 8000 | Check up contact points, wear and condition of corrosion. Measure the interior diameter and renew it by the follow Table 3. |  | 9.1 Periodic Inspection |  |  | 8000 | 8000
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 2 |  |  | CENTRIFUGAL PUMPS | Shaft coupling bolts and rubber ring | Check up condition of wear and renew if abnormal points are found. | INSPECTION | 12 | MONTHLY | 8000 | Check up condition of wear and renew if abnormal points are found. |  | 9.1 Periodic Inspection |  |  | 8000 | 8000
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 2 |  |  | CENTRIFUGAL PUMPS | Gear coupling | Replace grease. | REPLACEMENT | 6 | MONTHLY |  | Replace grease. *Replace grease first time in one month after operation start up, or 500 hours operation. *Type of grease: JIS K 2220 central lubrication grease Type 4 No.1, or equivalent. *Grease amount: See Table 4. |  | 9.1 Periodic Inspection | 1 | Monthly
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 12 |  |  | CENTRIFUGAL PUMPS | Mechanical Seal | Replace Mechanical Seal | REPLACEMENT |  |  |  | Replace mechanical seal when the allowable leak amount is exceeded. For Water (N): 3 cc/Hr (1 drop/min.) continuous dripping. For Water (Y): 5 cc/Hr (1 drop/30-40 sec.) continuous dripping. For Hot water (N): 3 cc/Hr (1 drop/min.) continuous dripping. For Hot water (N): When 3 cc/Hr (1 drop/sec.) continues more than 24 Hrs. and it does not seem to be decreased, OR when 1 cc/Hr (1 drop/3 sec.) or more is increased. For Hot water (Y): 5 cc/Hr (1 drop/30-40 sec.) continuous dripping. |  | b-2 Leak Amount and Determination of Replacing Time
G-03_INSTRUCTION_MANUAL_OF_CENTRIFUGAL_PUMPS_2.PDF | 12 |  |  | CENTRIFUGAL PUMPS | Gear Coupling | Replace grease in gear coupling | REPLACEMENT |  |  |  | Apply grease on the tooth faces of inner and outer cylinders thoroughly before assembling, and grease up to the specified level from the grease port. Grease may be deteriorated depending on the service conditions, and therefore it should be replaced at appropriate intervals. |  | c-2 Assembling Sequence